## ACH50 Calc - Eng units
Minneapolis Blower Door Sizing Calculation
|  |  |  | Date: | 2024-12-04
Enter Blue Fields (B7 & C7)
Fan Calculator - Application Info using Volume
Expected Air Permeability | Conditioned Volume | Max Envelope Leak Rate | Leak rate w/20% extra
ACH 50 | ft3 | CFM50 | CFM50
5 | 240000 | 20000 | 24000
Blower Door Fans |  | Fan Peak Output (CFM) |  |  | Results (Fan Rating @ 50Pa)
Make | Model | Free Air | 50 Pa | 75 Pa | # of Fans (Calc) | # Fans (Round-up) | # of Gauges
Minneapolis (TEC) | Model 3 | 6300 | 5350 | 4900 | 3.7383 | 4 | 3
Fan Rating w/20% "Headroom"
Pressure at expected air permeability using 1 fan |  | 6.5622 | Pa |  | # of Fans (Calc) | # Fans (Round-up) | # of Gauges
[5 empty] | 4.486 | 5 | 3
Option for Cell C6 - Assuming a simple Cube estimate of building volume
Floor Sq. Footage | 24000 | ft2
Building Enclosure Height | 10 | ft
Conditioned Volume | 240000 | ft3 | <----- This goes in cell C6
2400

## Enclosure Area - Eng units
Minneapolis Blower Door Sizing Calculation
|  |  |  | Date: | 2024-12-04
Enter Blue Fields (B7 & C7)
Fan Calculator - Application Info using Envelope Area
Expected Air Permeability | Envelope Area (of Conditioned Space) | Max Envelope Leak Rate | Leak rate w/20% extra
CFM50/ft2 | ft2 | CFM50 | CFM50
0.4 | 45000 | 18000 | 21600
Blower Door Fans |  | Fan Peak Output (CFM) |  |  | Results based on Fan Rating |  |  | Results based on Fan Rating w/20% "Headroom"
Make | Model | Free Air | 50 Pa | 75 Pa | # of Fans (Calc) | # Fans (Round-up) | # of Gauges | # of Fans (Calc) | # Fans (Round-up) | # of Gauges
Minneapolis (TEC) | Model 3 | 6300 | 5350 | 5000 | 3.6 | 4 | 3 | 4.0374 | 5 | 3
Option for Cell C6 - Simple Math Assumption for Calculating Envelope Area
L (ft) | W (ft) | H (ft)
100 | 100 | 26
Floor | 40 | ft2
Ceiling | 40 | ft2
(2) Long Walls | 80 | ft2
(2) Short Walls | 128 | ft2
Total Envelope Area | 288 | ft2 | <----- This goes in cell C6

## Understanding Sizing Results
| Q = k * (dp)^0.65 |  | 1.5385
|  | DP (Pa) | Q (CFM)
| Calculate Q | 50 | 5350
Understatnding # of fan calculation results |  | 25 | 3409.4497
| Calculate DP | 50 | 7500
This fan calculation is based on using the fans rated flow at 50Pa to determine if it can meet the pressure at the expected leak rate of the building. |  | 29.7194 | 5350
If the fan cannot reach 50Pa, that may be acceptable, depending on the goal of the measurement. It is still possible to get an estimate of the CFM50 even if the pressurization or depressurization achieved is less than 50Pa.
If you were not able to depressurize the building by approximately 50 Pascals (with the “open fan” running at full speed) because the building is extremely leaky, use the following instructions:
For DG-1000 and DG-700 Users No adjustments to the test procedure above are necessary other than to make sure the gauge was in the PR/ FL @50 mode during the one-point test.
The CFM50 leakage estimate will automatically be displayed on Channel B.
The leakage estimate shown on Channel B is determined by continuously adjusting the measured air flow from the blower door fan to a test pressure of 50 Pascals,
using the real-time Channel A building pressure reading and estimating the CFM50 using an exponent of 0.65 for the flow equation.
In practice, a building may have an exponent from 0.5 to 0.75. Since we are extrapolating the CFM50 from a lower pressure using an estaimted exponent of 0.65, there is some additional error. This is desribed below.